Specifier Notes:  This product guide specification is written according to the Construction Specifications Institute (CSI) 3-Part Format, including MasterFormat, SectionFormat, and PageFormat, as described in The Project Resource Manual—CSI Manual of Practice, Fifth Edition.

This section must be carefully reviewed and edited by the Architect or Engineer to meet the requirements of the project and local building code.  Coordinate this section with other specification sections and the Drawings.  Delete all “Specifier Notes” after editing this section.

Section numbers are from MasterFormat 2010 Update.

SECTION 26 05 83.11

WIRING CONNECTIONS: SOLDERLESS CRIMP CONNNECTORS

Specifier Notes:  Delete any information below in Parts 1, 2 or 3 which is not required or relevant for the project.

PART 1 – GENERAL

1.01	SUMMARY

A.	This section includes solderless crimp style connectors for terminating and splicing wire.

B.	Related Sections:

1.	Section 26 50 83.12 	Wiring Connections: Compression Lugs, Splices and Connectors

2. 	Section 26 05 83.13 	Wiring Connections: Crimp Tools for Solderless Connectors

1.02	REFERENCES

A.	Underwriters Laboratories, Inc. (UL):

1.	UL486A/B:      		Wire Connectors

2.	UL486C		Splicing Wire Connectors

3.	UL310			Electrical Quick Connect Terminals

B.	Canadian Standard Association (CSA):

- CSA C22.2-65 	Wire Connectors

- CSA C22.2-188 	Splicing Wire Connectors

- CSA C22.2-153 	Quick Connect Terminals

4.	CSA C22.1		Canadian Electrical Code Part I (CEC)

C.	National Fire Protection Association (NFPA):

1.  	NFPA 70	 	National Electrical Code (NEC)

D.	Society of Automotive Engineers (SAE)

1.	SAE AS7928		Terminals, Lug: Splices, Conductor: Crimp Style, Copper, General

Specification For

1.03	SUBMITTALS

A.	Comply with Section 01 33 00 – Submittal Procedures.

B.	Product Data:

1. Submit manufacturer’s descriptive literature and product specifications for each product.

2. Manufacturer’s product drawings.

C.	Manufacturer’s installation instructions

1.04	QUALITY ASSURANCE

A.	Manufacturer Qualifications: Products shall be free of defects in material and workmanship.

- Furnished products are listed or classified by third party agencies as being suitable for the intended purpose.

  - WARRANTY

- Product is warranted free of defects in material and workmanship.

- Product is warranted to perform the intended function within design limits.

PART 2 – PRODUCTS

2.01	GENERAL

A.	The solderless connectors shall include the following types:

1. 	Standard solderless nylon and vinyl insulated and non-insulated terminals, splices and connectors for the termination and splicing of wires for power and control circuits.

2. 	Fluoroploymer insulated ring terminals and splices for high temperature and radiation resistant environments.

3.   	Non-insulated nickel alloy terminals (NW Series) for use with nichrome wire in high temperature environments.

4. 	High temperature wire joints for multi-wire terminations.

B.	Terminals, splices and connectors shall be UL Listed and/or CSA Certified.

C.	Terminals, splices and connectors shall use the appropriate crimping tool and die in order to assure the correct mechanical and electrical connection.

D.	Terminals, splices and connectors shall be approved for nuclear facilities as commercial grade product.

2.02	MANUFACTURERS

A.	Acceptable Manufacturers:

Thomas & Betts Corporation

8155 T&B Blvd

Memphis, TN 38125

800-816-7809, 901-252-5000

www.tnb.com

Product:	Sta-Kon® Terminals

2.03	DESIGN AND PERFORMANCE REQUIREMENTS

A.	Standard insulated and non-insulated terminals, splices and connectors:

1.          Standard insulated terminals, splices and connectors shall have insulators molded or

extruded from nylon or vinyl materials.

2. 	Standard insulated (nylon and vinyl) and non-insulated terminal wire ranges shall be:

Insulated Red (RA type) and non-insulated (A type): 22-16 AWG

Insulated Blue (RB type) and non-insulated (B type):18-14 AWG

Insulated Yellow (RC type) and non-insulated (C type): 12-10 AWG

3.	Standard insulated (nylon and vinyl) and non-insulated quick disconnect connector wire ranges shall be:

Insulated Red (RA type) and non-insulated (A type): 22-18 AWG

Insulated Blue (RB type) and non-insulated (B type):16-14 AWG

Insulated Yellow (RC type) and non-insulated (C type): 12-10 AWG

4.	Standard insulated (nylon and vinyl) and non-insulated splice wire ranges shall be:

Insulated Red (RA type) and non-insulated (A type): 22-18 AWG

Insulated Blue (RB type) and non-insulated (B type):16-14 AWG

Insulated Yellow (RC type) and non-insulated (C type): 12-10 AWG

5.	#22 to #10 AWG insulated nylon and vinyl terminals shall be available in the following wire entry diameters;

a.	standard nylon: RA = 0.136”, RB = 0.162”, RC = 0.210”

b.	expanded entry nylon: RB = 0.190”, RC = 0.250”

c.	standard vinyl: RA = 0.150”, RB = 0.170”. RC = 0.210”

d.	expanded entry vinyl: RA = 0.170”, RB = 0.200”, RC = 0.250”

6.  	Large nylon and non-insulated terminals shall support wire sizes in the range from #8 AWG to 250 MCM (insulated: RD thru RM type; non-insulated D thru M type).

7.	Large vinyl insulated terminals shall support wire sizes #8 AWG (RDV type) and #6 AWG (REV type).

8. 	Parallel splices shall support wire range combinations from 22 AWG to 500 MCM (A thru R type).

9.	Wire joints shall support wire range combinations from 22 AWG to 10 AWG (RB, RC and RP series).

10.	Terminal and connector construction styles shall be: ring, rectangular, fork (standard, locking, flange), open barrel ring, butt splice, parallel splices, quick connect disconnects (male and female), pin terminals, ferrules, closed end wire joints.

11.	Standard quick disconnects (male and female) shall be available in 0.250” and 0.187” tab sizes.

12.	Standard terminals, splices and connectors shall be made from electrolytic copper for high conductivity.

- Standard terminals, splices and connectors shall be tin-plated to a minimum thickness of

0.0003”.

14. 	Standard #22 to #10 AWG size terminals and splices shall have internal serrations for lower resistance and increase wire pullout strength.

15.      	Standard terminals, splices and connectors shall have a chamfered wire entry for improved wire insertion.

16.      	Standard #22 to #10 AWG size terminals shall be selectively annealed to leave the barrel soft for crimping and the tongue (terminal) strong to resist bending.

17.	Standard terminals shall be tin-plated with a minimum 0.0003” plating thickness.

18.	Standard #22 to #10 AWG size nylon terminals and connectors shall have a metal sleeve to grip wire insulation.

19.	Standard #22 to #10 AWG size terminals barrels shall have an overlapped seam for nylon insulated terminals and a brazed seam for vinyl insulated terminals.

20.	Standard terminals and connectors shall be identified with the T&B logo, stud size and wire size.

21. 	Standard splices shall be identified with the T&B logo, stud size and wire size.

22.	Standard insulated terminals, splices and connectors shall have a maximum temperature rating of 105ºC and maximum voltage rating of 600V.

23. 	Standard non-insulated terminals, splices and connectors shall have a maximum temperature rating of 150°C.

24.	Standard wire entry nylon terminals RA, RB, RC types, large nylon terminals RD to RM types, large non-insulated terminals D to M types, and non-insulated rectangular tongue terminals A, B, C types shall be military listed to SAE AS7928,  Reference military QPL-7928 for complete details.

B	Fluoropolymer insulated ring terminals and splices:

1.	Fluoropolymer insulated ring terminals shall be the RAT, RBT and RCT series.

2.	Fluoropolymer insulated splices shall be RAAT21, RBBT21 and RCCT21 catalog numbers.

3. 	Insulators shall be extruded from Fluoropolymer, a UL94-V0 radiation resistant material.

4.	Ring terminals and splices shall have a maximum temperature rating of 150ºC.

5. 	Ring terminals and splices shall have a maximum voltage rating of 600V.

6.          The insulators shall be co-extruded with a color strip indicating the wire range.

Red: 22-18 AWG (A type)

Blue: 16-14 AWG (B type)

Yellow: 12-10 AWG (C type)

7.	Ring terminals and splices shall be made from electrolytic copper for high conductivity.

8.	Ring terminals and splices shall be tin plated to a thickness of 0.0003” minimum.

9.	Ring terminals shall have a metal sleeve to grip wire insulation.

10. 	Ring terminals and splices shall have internal serrations for lower resistance and increased wire pullout strength.

11.      	Ring terminals and splices shall have a chamfered wire entry for improved wire insertion.

12.      	Ring terminals shall be selectively annealed to leave the barrel soft for crimping and the tongue strong to resist bending.

13. 	Ring terminals shall be identified with the T&B logo, stud size and wire size.

14.        The approved tool for crimping shall be WT145C.

C.	Non-insulated Nickel Alloy Terminals (NW Series):

1.	Terminal construction shall be a ring with stud sizes from #6 to #12 bolt hole.

- Terminals shall accept nichrome wire sizes 24 AWG to 10 AWG.

- Terminals shall be made from a nickel alloy.

- Terminals shall have a maximum temperature range of 1200ºF (649ºC).

- Terminals shall have internal serrations for lower resistance and increased wire pullout strength,

- Terminals shall be an open barrel construction.

- Terminals shall be identified with the T&B logo and NW

- The approved tool for crimping shall be WT1377.

D.	High Temperature Wire Joints:

- High temperature wire joints shall be rated for 150ºC, 600V maximum.

- High temperature wire joint insulators shall be molded from a nylon 4.6 material with a

UL94-V2 flame rating.

3. 	High temperature wire joints shall be available in three size and accept the following combination of wires and ranges:

T&B Cat. No.	Wire Combinations & Sizes

RB4-HT	2#18 AWG to 2#16 AWG

RC6-HT	3#16 AWG to 3#14 AWG

RP7-HT	3#14 AWG to 3#12 AWG

4.	High temperature wire joints shall use a brazed copper sleeve with internal serrations for increased conductivity and wire pull out resistance.

5.	High temperature wire joint crimp sleeves shall be made from electrolytic copper for high conductivity.

6.  	High temperature wire joints will have a light green color and shall have the T&B logo molded into the insulator.

7. 	The approved tool for crimping shall be:

T&B Cat. No.	T&B Tool

RB4-HT	WT2000

RC6-HT	ERG4001

RP7-HT	WT2130A

PART 3 – EXECUTION

3.1	INSTALLATION

A. 	Installation shall be in accordance to the NEC, CEC and manufacturer’s tool instructions.

1. 	Terminals, splices and connectors shall have the termination wire stripped to the proper

length as defined in manufacturer’s literature.

B. 	Unless otherwise specified all terminals, splices and connectors shall be installed with one of the

following tools:  Reference manufacturer’s literature and section 26 05 83.13 for more details.

1.	WT2000 (plier hand tool) – RA, RB, RC insulated terminals, splices, quick disconnects and wire joints; A, B, C non-insulated terminals, splices and quick disconnects.

2.	ERG4001 (hand tool) – RA, RB, RC insulated terminals, splices and quick disconnects.

3.	ERG4002 (hand tool) – A, B, C non-insulated terminals, splices and quick disconnects.

4.	ERG4007 (hand tool) – RDV and REV vinyl insulated terminals.

5. 	BAT22-6 (battery hand tool) - #22 to #6 AWG insulated and non-insulated terminals, splices

and quick disconnects.

6. 	PAIR22-6 (pneumatic hand tool) - #22 to #6 AWG insulated and non-insulated terminals,

splices and quick  disconnects.

7.	BAIR22-6 (bench mount air tool) - #22 to #6 AWG insulated and non-insulated terminals,

splices and quick disconnects.

8.  	25000 (bench mount air tool) - #8 – 250 kcmil non-insulated and nylon insulated terminals

and splices.

- 13400 (hydraulic crimping head) - #8 – 250 kcmil non-insulated and nylon insulated terminals

and splices, requires either pump 13610A or 13810.

END OF SECTION